## Live Status
Toronto Dominion Bank Tower
Elevator | Group | Reason | Date out of Service | Thyssen Contacted | Smart IP | Ticket Number | Time Service Call to Thyssen was Placed (for After Hours & Critical Elevator Use Only) | Time Thyssen Arrived On Site (for After Hours & Critical Elevator Use Only) | Time Elevator was Placed Back in Service by Thyssen (for After Hours & Critical Elevator Use Only) | Status | Expected Return to Service | Actual Return to Service Date
33 | Freight | Rope replacement and elevator pit flood | 2014-05-15 | Locked out by TKE | [5 empty] | Sept 10 - ropes to me measured Sept 11th and then re-roping required
5 | LR | NF - Elevator # 5 on S.F.T mode doors closed lobby level. Called in by lobby desk Jacob | 18th Dec 2014 @ 4.35 pm | Yes - Service Desk |  | 942654 |  |  |  | Reported to be online at 0424hrs 15/01/07 -CF
2 | LR | Went on DRF mode and got stuck on 7 floor with doors closed. | 2014-12-22 | Yes - Service Desk |  | 946834 |  |  |  | Reported to be online at 0424hrs 15/01/07 -CF
7 | LR | Elevator Entrapment - 66 Wellington St. West - Elevator #7 | 2015-01-05 | Yes - Service Desk and Thyssen Contact on site |  | 998959 |  |  |  | All Clear from elevator Entrapment - 66 Wellington St. West - Elevator #7 started at 1155HRS patron left elevator on main lobby at 1204HRS duration: 9 minutes personal information: Anne Choi from TD Bank/7th Flr at TD Bank Tower
10 | ML | Unresponsive on 28th floor. Doors open. | 2015-01-03 | Yes |  | 995320 |  |  |  | Returned to Service on Jan. 7/15
21 | HR | Stuck on 31st floor doors open CSD mode | 2015-01-05 |  |  | 996662 |  |  |  | Reported to be online at 0424hrs 15/01/07 -CF
3 | LR | drops quickly from the 3rd floor to the lobby. It is currently placed out of service. | 2014-01-06 | Yes - Service Desk |  | 1018402 |  |  |  | Reported to be online at 0424hrs 15/01/07 -CF
12 | LR | Lobby desk - Elevator #12 is o/s on DSC mode, doors open on lobby level. | 2014-01-07 | Yes - Service Desk Jan 7th @ 10:43 am |  | 1019376
9 | LR | on DSC mode, doors open on the 30th fl. | 2014-01-07 | Yes - Service Desk |  | 1019625
4 | LR | on DRF mode, doors closed on the 8th fl. | 2014-01-07 | Yes - Service Desk |  | 1019625
TD North Tower
Elevator | Group | Reason | Date out of Service | Thyssen Contacted | Smart IP | Ticket Number | Time Service Call to Thyssen was Placed (for After Hours & Critical Elevator Use Only) | Time Thyssen Arrived On Site (for After Hours & Critical Elevator Use Only) | Time Elevator was Placed Back in Service by Thyssen (for After Hours & Critical Elevator Use Only) | Status | Expected Return to Service | Actual Return to Service Date
81 | Shuttle | Out by TKE for refurbishment and modernization | 2014-11-24 | [7 empty] | January 1st, 2015
69 | HR | Problem with drive fault | 16DEC14 | yes |  | 939645 | 0557 hours on December 17, 2014
76 | Small Freight | Entrapment | 2014-12-18 13:51 |  |  | 942339 |  | 18:02:00 18-12-14 |  | escorted up by Farya. Elevator not put back in service
72 | HR | Entrapment | 18/12/2014 | Yes- Dispatch |  | 942838 | 22:38:00 Dec. 18/14 | 22:53:00 Dec. 18/14
63 | MR | Stuck on C/C doors closed | 2015-01-02 | Yes- Dispatch |  | 995305 |  |  |  | Reported to be online at 0424hrs 15/01/07 -CF
59 | MR | Entrapment | 2015-01-05 | Yes |  | 996631 |  |  |  | Reported to be online at 0424hrs 15/01/07 -CF
TD West Tower |  | Currently not working
Elevator | Group | Reason | Date out of Service | Thyssen Contacted | Smart IP | Ticket Number | Time Service Call to Thyssen was Placed (for After Hours & Critical Elevator Use Only) | Time Thyssen Arrived On Site (for After Hours & Critical Elevator Use Only) | Time Elevator was Placed Back in Service by Thyssen (for After Hours & Critical Elevator Use Only) | Status | Expected Return to Service | Actual Return to Service Date
83 | LR | Went on DRF mode and got stuck on 10th floor with doors open. | 2015-01-07 | Yes |  | 1020746
TD South Tower |  | Currently on 18th floor with doors open and lights turned off. IND mode.
Elevator | Group | Reason | Date out of Service | Thyssen Contacted | Smart IP | Ticket Number | Time Service Call to Thyssen was Placed (for After Hours & Critical Elevator Use Only) | Time Thyssen Arrived On Site (for After Hours & Critical Elevator Use Only) | Time Elevator was Placed Back in Service by Thyssen (for After Hours & Critical Elevator Use Only) | Status | Expected Return to Service | Actual Return to Service Date
104 | LR | Car # 104(Low rise) out of service since Sunday December 28, 2014 at 11:36 am - Elevator keeps ringing with doors opening and all buttons are lit. Car is on lobby level, doors open and lights off. | 2014-12-30 | Nf - Dec 30th - Yes Service Desk @ 8:13 am |  | 965412
125 | Small up Escalator | Showing Error (ER) | 2015-01-02 | Yes |  | 994776 |  |  |  | Reported to be online at 0424hrs 15/01/07 -CF
114 | HR | Offline Overnight
115 | HR | Offline Overnight
113 | HR | Out by TKE for refurbishment and modernization | 2014-09-30 | [7 empty] | December 2014
107 | LR | Out by TKE for refurbishment and modernization | 2014-10-08 | [7 empty] | December 2014
117 | Freight | Entrapment | 2015-01-07 |  |  | 1019018 | 0136hrs | 0142hrs | 0147hrs | Offline
Ernst & Young Tower |  | Dec 29 (1 day ago)
Elevator | Group |  | Date out of Service | Thyssen Contacted | Smart IP | Ticket Number | Time Service Call to Thyssen was Placed (for After Hours & Critical Elevator Use Only) | Time Thyssen Arrived On Site (for After Hours & Critical Elevator Use Only) | Time Elevator was Placed Back in Service by Thyssen (for After Hours & Critical Elevator Use Only) | Status | Expected Return to Service | Actual Return to Service Date
139 | HR | Stuck on an unknown level, discovered by security during routine status checks | 2014-12-31 | yes |  | 983092
130 | LR | NF - Low Rise has gone Out of Service Doors closed. Stuck in the shaft between 5th floor & lobby | 2015-01-05 | Yes Service desk @ 11:11 am |  | 998141 |  |  |  | Reported to be online at 0424hrs 15/01/07 -CF
95 Wellington Tower
Elevator | Group | Reason | Date out of Service | Thyssen Contacted | Smart IP | Ticket Number | Time Service Call to Thyssen was Placed (for After Hours & Critical Elevator Use Only) | Time Thyssen Arrived On Site (for After Hours & Critical Elevator Use Only) | Time Elevator was Placed Back in Service by Thyssen (for After Hours & Critical Elevator Use Only) | Status | Expected Return to Service | Actual Return to Service Date
201 | HR | Complaint, tenant reported stopping on random floors. | 2015-01-07 | yes |  | 1020747
203 | HR | Unresponsive on 15, doors closed | 2015-01-06 | Yes |  | 1018888 |  |  |  | Back online as per TRR Duque-Biddle |  | Wed Jan 07/15 at 0824 hours

## TD Bank Tower (Tower #1) Histor
Elevator | Group | Reason | Date out of Service | Thyssen Contacted | Smart IP | Ticket Number | Time Service Call to Thyssen was Placed (for After Hours & Critical Elevator Use Only) | Time Thyssen Arrived On Site (for After Hours & Critical Elevator Use Only) | Time Elevator was Placed Back in Service by Thyssen (for After Hours & Critical Elevator Use Only) | Status | Expected Return to Service | Actual Return to Service Date
12 | Low-Mid | Entrapment on 19th floor (under construction/demolition). Currently on 19th floor with doors open. CSD mode. | November 28, 2013 1116hrs | [6 empty] | Returned to service
25 | Freight | Went on DRF mode and got stuck on 4th floor with doors open. Current status is the same. | 2013-12-18 | Yes |  | 522450 |  |  |  | Restored same day at 2200 hours.
10 | ML | Shut Down due to complaints of screeching noise. | 12/31/2013 1259hrs -CF | To Assist advised - KH Jan 2- Lucy advised Kevin via phone Dec 31st | [5 empty] | KH - Back in Service Jan 6th 8:10am per Rita at lobby desk
Up Escalator(#4) |  | east side handrail making unusual loud squeaky whistling noises. | 1/2/2014 -CF | Yes |  | 530082 |  |  |  | Back in service
25 | HR | DRF Mode | 2014-01-07 | Yes |  | 543069 |  |  |  | Back in service
6 | LR | DIS | 2014-01-03 | Thyssen advised Jan 3rd
34 | Freight | Went on DSC mode and got stuck on 55th floor with doors open. Current status is the same. | January 7, 2014 0142 hrs | Yes |  | 542137 |  |  |  | Back in service
10 | Escalator | Shut off due to loud grinding noise | 2014-01-09 | Kristina spoke to Kevin and Julieta |  | YES |  |  |  | Back in Service
13 | ML | DRF Mode | 08JAN14 | [6 empty] | KH -Back in service January 14th at 11am per lobby desk
25 | high rise | Went on DRF mode and got stuck on 4th floor with doors open. Current status is the same. | 2014-01-15 | Yes |  | M551 |  |  |  | Found to be working at 0519hrs 14-01-20 -CF
9 | Lowrise | Went on DRF mode and got stuck on 24th floor with doors open. Currently on 20th floor with doors open and lights turned off. IND mode. | 2014-01-15 | Yes | [5 empty] | Found to be working at 0519hrs 14-01-20 -CF
3 | lowrise | Went of DRF with near entrapment on the 11th floor | 2014-06-03 | yes |  | MATT ADVISED | [5 empty] | 23/01/14
3 | low-rise | Went on DRF mode on the 11th floor and caused a near entrapment. Currently on the same floor with doors closed. DSC mode. | 2014-03-06 | Yes by Tenant Relations | [5 empty] | Back in service
1 | Low rise | offline on 19 w/ doors closed, not responding | March 21 | Yes Immediate service |  | 638223 |  |  |  | Car # 1 was back in-service on March 22, 2014 at 1640 hrs.
32 | HR | CSD mode on 32 w/ doors open. -CF | 3/13/2014 1750hrs | Yes - For daytime service |  | 627220 |  |  |  | Reported working on March 20 1514hrs.
31 | High-rise | Got stuck on shear wall between ground lobby and 44th floor and 12 occupants became entrapped. Currently on ground lobby with doors closed. INS mode. | 3/24/2014 | YES | [5 empty] | Back in service
26 | High-rise | Maintenance by Thyssen. Currently on 44th floor with doors closed. DSC mode. | March 28, 2014 | maintenance by thyssen | [5 empty] | Already reported to be functional yesterday April 1
41 | parking | No Communication from the car to SOC | 4/5/2014 |  | needs to be contacted |  |  |  |  | KH - April 7 - reported working by Rita at lobby desk 7:35am -- Per e-mail from Sean Landry changed to immediate service 14-4-6 1438hrs. Reference #677434
31 | high-rise | To Assist advised to shut down as per Allison Stryland | 4/3/2014 | YES | [5 empty] | KH April 7th - per Rick, waiting for authorization from Allison to put back in service. Back in service.
24 | Mid Rise | Went on SFT mode on ground lobby and 14 people became entrapped. Currently on ground lobby with doors closed. INS mode. | 2014-04-11 | YES | [5 empty] | Functional as of April 14 1445hrs -CF
5 | Low Rise | Went on SFT mode on 7th floor and 2 people became entrapped. Currently on 7th floor with doors closed. IND mode. | 2014-04-11 | YES | [5 empty] | Reported to be functinal at 0355hrs 14/4/24. -CF
13 | Low-mid | SFT mode, unknown reason | 2014-04-22 | YES | [5 empty] | April 23 - TKE working on |  | Car # 13 went back in-service on May 5, 2014 at 1432 hrs.
11 | Mid low | Went on INS mode and got stuck on 31st floor with doors closed. | 2014-05-13 | Yes |  | 711364 |  |  |  | Car # 11 went back in-service on May 14, 2014 at 1400 hrs.
28 | high-rise | Complaint of dropping to 50th floor before it goes up to the next floor from 50-53. Currently on 53rd floor with doors closed. DSC mode. | 2014-03-20 | Out for repairs by Thyssen | [5 empty] | Back in service
32 | high-rise | Currently on 53rd floor with doors open. DSC mode. | 2014-05-29 | yes |  | 728303 |  |  |  | Back in service |  | 2014-05-30
9 | mid low | Went on DRF mode and got stuck on 29th floor with doors open. Currently on 19th floor with doors open and lights turned off. INS mode. | 2014-06-09 | yes |  | 738392 |  |  |  | Car # 9 went back in-service on June 10, 2014 at 1030 hrs
4 | low rise | Went on SPR mode and got stuck on ground lobby with doors closed. Current status is the same. | 2014-06-09 | yes |  | 738392 |  |  |  | Car # 4 went back in-service on June 10, 2014 at 0756 hrs.
29 | High rise | Replacing governor (machinery, a device for maintaining uniform speed). Currently on 53rd floor with doors closed. DIS mode. | 2014-05-27 | YES |  | 723667 |  |  |  | Reported to be functional at 0355hrs 14/6/13 -CF
19 | Mid high | Shut Down for maintanance by Thyssen for Ainsworth | 2014-06-23 | [6 empty] | Car # 19 went back in-service on June 24, 2014 at 1454 hrs
29 | High Rise | Complaint of scraping noise. Currently on ground lobby with doors closed. INS mode. | 2014-07-03 | [6 empty] | Car # 29 went back in-service on July 4, 2014 at 1000 hrs
42 | TD Mailroom Concourse | Entrapment on 07/07/14 at approximately 1115 hours between floors concourse and P1 | 2014-07-07 | Yes |  | (ref # 766466) |  |  |  | Back in service
31 | HR | SFT mode on L w/ doors closed | 2014-07-20 | Yes at 1126hrs 14/07/20 |  | 777325 |  |  |  | CF - Thyssen arrived at 1157hrs and repaired the elevator at 1255hrs. KH - reported to be working July 21st 8am
3 | LR | On the 12th floor w/ doors closed. DIS mode | 2014-07-21 2317hrs | Yes at 0020hrs |  | 778457 |  |  |  | NF - Elevator 3 is back in service was taken out by Thyssen for Maintenance yesterday afternoon - Claudia Raso 9:42 AM
28 | High Rise | Went on DRF mode and got stuck on 48th floor with doors open. Currently on 54th floor with doors closed. DSC mode. | 2014-06-05 | YES |  | 735844 |  |  |  | KH - Elevator out due to tenant complaint of shaking and dropping June 5th |  | Back Service July 23rd 8:56am
7 | LR | ON the 16th floor w/ doors closed. DIS mode. | 2014-07-22 | Maintanance per Thyssen | [5 empty] | Back in service July 24th 7:50am per Claudia at lobby desk
5 | LR | DSC on lobby | 2014-07-28 | Yes |  | 783836 |  |  |  | Back in service
1 | LR | out of service | 2014-08-06 | toassist called | [5 empty] | Car # 1 went back in-service on the same day at 1706 hrs
9 | MR | Went on DRF mode and got stuck on ground lobby with doors closed. | 2014-08-08 | Yes |  | 798236 |  |  |  | Back in service
29 | HR | Complaint of loud scraping noise. Also, very shaky, and independent key switch does not work. | 2014-04-09 | Yes | [5 empty] | Reported to be online at 1600hrs 14-09-05 |  | Before Sept 08/14
30 | HR | Not responding, on 45 w/ doors closed | 2014-09-06 | Yes |  | 827854 |  |  |  | reported to be working at 0600hrs 14-09-07 -CF |  | Before Sept 08/14
20 | MHR | Bumpy ride. Thyssen took it out of service till Monday | 2014-08-29 | [6 empty] | Back in service Sept 11 | Sept. 10th | Sept 11/14
18 | MR | Taken out of service by Thyssen due to complaint of loud noise | 2014-09-11 | YES | [5 empty] | Back in service
34 | Freight | Rope replacement | 2014-09-03 | Yes |  | 823722 |  |  |  | Back in service
Down Escalator |  | Knocking sound and loose comb segment at bottom end | September 16,2014 | Yes |  | 835382 |  |  |  | Reported to be working at 0833hrs 14-09-16
1 | LR | Not responding to calls, on 2 w/ doors open. CSD mode | september 16,2014 | Yes |  | 835386 |  |  |  | Reported to be working at 0821hrs 14-09-16
30 | HR | Taken out of service by Thyssen due to complaint | 2014-03-05 | YES | [5 empty] | Back in service
12 | ML | Stuck on 26 | 2014-09-23 | Yes |  | 842371 |  |  |  | back in service |  | 2014-09-24
20 | Mid Low | Poor Communication (on 19, doors open) | 9/27/2014 |  | Yes - Voicemail |  |  |  |  | On 32 w/ doors open and lights off
32 | HR | Out by Thyssen for maint. | 2014-09-11 | [6 empty] | 53rd, doors closed, dsc mode |  | Oct. 1st 11:24am
26 | HR | Entrapment | 2014-09-28 | [6 empty] | Moving to random floors without being called but doors are staying closed | Back in service Oct 6th 2:25pm
6 | LR | CSD Mode - on 3rd floor | 9/19/2014 | Yes - Thyssen Dispatch |  | 839577 |  |  |  | on 19, INS mode |  | 2014-10-08
34 | Freight | SFT Mode - Between Lobby and 2nd floor | 2014-10-09 | Yes - Thyssen Dispatch |  | 862585 |  |  |  | Back in service 8:45am Oct 9th
34 | Freight | Stuck on 5th floor, doors closed | 10/9/2014 | YES - Service desk as well as on site tech |  | 862863 |  |  |  | Back in service
13 | LR | Entrapment - sitting on the 19th floor doors closed | 10/7/2014 | Yes | [5 empty] | Reported to be working at 0455hrs 14-10-15 -CF
33 | Freights | Elevator 34 is functional. Per Eric Turner Thyssen called to inspect elevator pits after floor |  | Yes, immediate service 1744hrs 14-10-11 |  | 864664 |  |  |  | KH - Oct 16 - no water found in pits per Eric T.
6 | LR | Stuck on 2nd floor CSD mode, Doors Open | 10/9/2014 | Yes - Rita M advised Matt at 8:23am | [5 empty] | Back in service
22 | MH | Entrapment | October 24, 2014 | Yes |  | 874627 |  |  |  | Back in service. |  | 2014-10-28
1 | LR | Not responding to floors P2 to 9. Only moves to floors 10 to 19 with pass card. | 11/01/14 | Yes - Dispatch - After Hours Service |  | 887393 |  |  |  | Back in service
28 | HR | Complaints about doors hitting tenants | 10/17/2014 | Yes - Dispatch - Regular Hours |  | 869510 |  |  |  | NF - Nov 4th- Rita Martel 11:25 AM (3 minutes ago) FYI Car #28 back in service at 11:22am
6 | LR | Stuck on 17 | 2014-11-04 | Yes |  | 893216 |  |  |  | Reported to be working at 0414hrs 14-11-06 -CF
20 | Hi-Mid | Out for maintenance by Thyssen | 2014-11-04 | Yes |  | As Per Thyssen |  |  |  | Reported to be working at 0414hrs 14-11-06 -CF
29 | HR | Out for repairs by Thyssen | 11/5/2014 | Locked out by TKE | [5 empty] | Reported to be working at 0455hrs 14-11-12 -CF
41 | Parking | Car #41 (parking) stuck on P1 with the doors open reading DRF mode | November 17, 2014 | Thyssen tech Rick notified ref #903038 | [5 empty] | Back in service
43 | TD Bank Private | Out by TKE for refurbishment and modernization | [7 empty] | Back in service | December 1st
26 | HR | Complaint of car bouncing on ground lobby and doors not opening immediately, delay of 5-10 seconds and door open button needed to be pressed. | 11/11/2014 | Yes |  | 898274 |  |  |  | Back in Service
6 | LR | Showing DRF on Ground | 2014-11-19 | Yes |  | 905370 | 2014-11-19 |  |  | back in service
26 | HR | Complaint received that the car bounced on ground then the doors hesitated to open | 11/19/2014 | Rita advised Matt as well |  | 905839 |  |  |  | Back in service
9 | Low rise | Went into CSD mode stuck on 24th floor with doors open. | November 15, 2014 |  |  | 902382 |  |  |  | Back in service
29 | HR | Banging on the 54th floor still in service - CAnnot be taken off service as per Security | November 24, 2014 | Spoke to Thyssen tech Matt directly |  | 910066 |  |  |  | Back in service
28 | HR | Tenant struck by a door on the 45th floor | November 24, 2014 | Spoke to THyssen Matt directly |  | 910191 |  |  |  | Back in service
8 | Low rise | Went on SPR mode and got stuck on 14th floor with doors closed. | November 25, 2014 |  |  | 913894 |  |  |  | Back in service
4 | Low rise | Went on DRF mode and got stuck on 5th floor with doors closed. | November 25, 2014 |  |  | 913893 |  |  |  | Back in service
34 | Freight | Stuck on lobby level doors open | Dec 1st 2014 @11:45am | Yes - Service desk & tech Matt |  | 923867 |  |  |  | Back in service 1:21pm Dec 1
34 | Freight | Stuck on lobby level doors open | Dec 1st 2014 @12.33 pm | Yes - Service desk & tech Matt |  | 923993 |  |  |  | Back in service 1:21pm Dec 1
34 | Freight | stuck on concourse level doors open | December 2, 2014 @ 2155 hours | Yes - Service Desk |  | 926972 | 2155 hours | 2300 hours | 0100 hours
16 | ML | CSD Mode on 19, doors open and lights off | 12/3/2014 1500hrs | [6 empty] | Back in service Dec 4 7:27am
23 | MH | While on service mode the elevator doors closed and it moved on it's own from 36 to 33. It has now been left on service on 37 w/ lights off | 2014-12-04 | Yes |  | 928071 |  |  |  | Back in service Dec 4 7:23am
8 | LR | SPR mode on 14 w/ doors closed | 2014-12-04 | Yes, Immediate |  | 928070 | 0453hrs |  |  | Back in service Dec 4 5:51am
9 | ML | stuck on the 21st floor CSD mode with doors open | November 27, 2014 @ 2.41 pm | Yes - Service Desk |  | 918458 |  |  |  | This elevator was found running at 0403hrs 14/12/09.
6 | LR | Not responding, unknown floor | 29NOV14 |  |  | 922768 |  |  |  | Was restored some time prior to December 5, 2014 |  | 2014-12-15
14 | LR | Tenant was inside and all the elevator buttons lit up. Then it went to floor 21 and the doors opened just a little bit, and he was trapped inside for a few seconds. Then it went up to his original floor which is the 25th floor. |  | Yes - Service Desk |  | 930463 |  |  |  | Back in service
18 | MH | Stuck on Lobby, doors open | 05DEC14 | Yes - Service Desk for Business Hours |  | 931625 |  |  |  | This elevator was found running at 0403hrs 14/12/09.
8 | LR | Stuck on 14, doors closed | 2014-12-06 | Yes |  | 931116 | 3:05 |  |  | Back in service
8 | LR | SPR mode on 14 w/ doors closed | 14/12/05 Afternoon | Yes, for daytime service |  | 932831 |  |  |  | Back in service
8 | LR | Julietta - DSC with doors closed on floor 2 | 9th Dec 2014 @ 2:35pm | Yes - Thysen Service desk |  | 933299 |  |  |  | Back in service
34 | Freight | Flooding from the 3rd floor entered the elevator shaft. There was a brief 2 minute entrapment as well but the doors opened on their own. | 2014-12-08 | Yes for immediate service |  | 932824 | 0223hrs 14/12/09 | 0625hrs 14/12/09 |  | Back in service Dec 11th |  | 2014-12-11
2 | LW | NF - Darell Elevator 2 has gone Out of Service on the 12th fl - DRF | 11th Dec 2014 @10.05 am | Yes - Service Desk |  | 935188 |  |  |  | Reported running by Julieta Dec 12th 8:14am
4 | LR | Elevator 4 Out of Service on 5th fl - CSD | 11th Dec 2014 @ 1:07 pm | Yes - Service desk |  | 935446 |  |  |  | Back in service
34 | Freight | DRF Mode | 12/12/2014 @ 0725 hours | Yes - Dispatch & Kevin |  | 936011 |  |  |  | On the 25th floor with doors closed |  | Dec 12th 8:53am
43 | Private Banking | Status unknown, not answering hall-calls | 2014-12-13 | Yes - Service Desk |  | 937225 | 23:33 |  | 7:05 | Back in service |  | 2014-12-14
27 | HR | Elevator Flood | 2014-08-05 | Locked out by TKE |  | 794294 |  |  |  | DRF mode, Lobby w/ doors closed. Back in service |  | 2014-12-15
6 | LR | Entrapment | 12/5/2014 0924hrs | Yes - Service Desk |  | 937449 | 0435HRS |  |  | On lobby level with doors closed. Back in service |  | 2014-12-15
12 | Mid Low | Near Entrapment | 12/11/14 @ 0903 hours | Yes - Dispatch & Rick |  | 935049 |  |  |  | On Lobby level with doors closed. Back in service
9 | ML | 28th floor, doors open | 15DEC14 | [6 empty] | Back in service
34 | Freight | Stuck on Concourse doors open | Dec. 19 2014 @ 0014 hours | yes - Thyssen |  | 942847 | 0015 hrs | 0059 hrs | 0125 hrs | returned to service
28 | HR | Shut down on Ground - Hit a McCarthy Employee. was exiting the car and the doors closed hard on her possibly injuring her. Security is en route to obtain a report and the car was shut down on ground. | November 27, 2014 @9.17 am | Yes - Service Desk |  | 917890 |  |  |  | Back in service January 5th 11am
7 | LR | DRF on 15th floor doors open | 2015-01-02 | Yes - Service Desk |  | 994744 |  |  |  | Back in service January 5th 8am

## TD North Tower (Tower #2) Histo
Elevator | Group | Reason | Date out of Service | Thyssen Contacted | Smart IP | Ticket Number | Time Service Call to Thyssen was Placed (for After Hours & Critical Elevator Use Only) | Time Thyssen Arrived On Site (for After Hours & Critical Elevator Use Only) | Time Elevator was Placed Back in Service by Thyssen (for After Hours & Critical Elevator Use Only) | Status | Expected Return to Service | Actual Return to Service Date
52 | low rise | The elevator is out of service on 2nd floor with doors closed, the elevator was placed out of service by thyssen technician for (re-roping) | 2013-11-20 | Taken out of service by Thyssen | [5 empty] | Found functional at 0524hrs 13-11-29. -CF
54 | Low | The elevator is out of service on 15 floor with doors open and lights off, the elevator went out of service on (DRF) mode (stopped responding) | Monday/January/06/2014 | Yes |  | 542118 |  |  |  | Reported to be working at 0518hrs 2014-01-08 -CF
62 | Mid | Out Of Service | 2014-01-01 | [6 empty] | Reported to be working at 0459hrs 2014-01-02 -CF
10 | Escalator | Shut off due to loud grinding noise | 2014-01-09 | Kristina spoke to Kevin and Julieta |  | YES |  |  |  | Back in Service
60 | Mid | (DSC), The elevator is out of service on lobby with doors closed, the elevator is out of service due to an elevator entrapment | Thursday/November/07/2013. | YES- Spoke to kevin | [5 empty] | Back in service
76 | Freight | stuck on P1 | 2014-01-10 | YES |  | 546555 |  |  |  | Back in service
54 | LR | SPR on 15 | 13JAN14 | yes |  | 547241 |  |  |  | Back in Service
73 | HR | IND on 45 | 2014-01-14 | yes | [5 empty] | Reported to be working at 0920hrs 14-01-17 -CF
51 | Mid Rise | DSC mode; out for testing as per Thyssen | 2014-01-22 | Yes | [5 empty] | back in service 23/01/14 |  | 23/01/14
62 | High rise | is on CSD mode & located on floor 19. | 2014-03-19 | [6 empty] | Reported to be working at 0413hrs 14-03-17 -CF
56 | Mid Rise | Went out of service, is now on 8th floor on DSC mode. | 2014-03-18 | Yes- Spoke to Rick | [5 empty] | Reported to be working at 0409hrs 14-03-21 -CF
74 | High Rise | The elevator is out of service on 40 floor with doors closed, the elevator is out of service due to elevator entrapment | 2014-03-25 | [6 empty] | Reported to be working at 0410hrs 14-03-27 -CF
63 | Mid rise | The elevator is out of service on concourse with doors open and lights off, the elevator was placed out of service due to a near elevator entrapment | 2014-03-28 | yes |  | 666458 |  |  |  | Reported to be working at 0410hrs 14-4-1 -CF
62 | MR | SPR mode on 26 w/ doors closed | 2014-04-02 | Yes - for regular business hours |  | 673535 |  |  |  | Back in service
60 | MR | The elevator is out of service on lobby with doors open and lights off, the elevator was placed out of service due to tenant complaint on 21st floor and 26 floor that they wait to long for the elevator to come to those floors, thyssen has came and checked the elevator and said to keep the elevator 60 out of service until they fix this | 2014-04-06 | KH - Spoke to Rick April 7th 7:50am |  | 677456 |  |  |  | Back in service
58 | LR | Out of service on lobby - Out by TKE for maintenance | 02APR14 | KH Spoke to Rick April 3rd 8:07am | [5 empty] | Back in Service
59 | Mid Rise | The elevator is out of service on lobby with doors closed | 2014-04-10 | Yes |  | 681457 |  |  |  | Back in service April 11th at 7:55am per lobby desk
63 | Mid Rise | The elevator is out of service on the 20th floor with doors closed, Please be advised that the elevator is showing in service on the elevator monitor but the elevator is not responding to the call button | 2014-04-10 | Yes |  | 681457 |  |  |  | Back in service April 11th at 7:55am per lobby desk
70 | High rise | The elevator is out of service on lobby with doors closed, Please be advised that the elevator is showing in service on the elevator monitor but the elevator is not responding to the call button, the elevator was discovered not responding | 2014-04-10 | Yes |  | 681457 |  |  |  | Back in service April 11th at 7:55am per lobby desk
53 | Low Rise | Placed out of service by lobby desk due to complaints of doors hitting people | 4/11/2014 11.20am | YES - KH Spoke to Kevin April 11th 11:25am | [5 empty] | Investigated by Kevin, no issues with doors, it is human error.Placed back in service April 11th
53 | Low Rise | DRF Mode - reported to Kristina by Rick and Kevin from TKE on April 14th |  | YES | [5 empty] | Back in service April 14th 12pm per lobby desk
62 | Mid Rise | Gets stuck for short period of times on 29th | 2014-04-15 | yes |  | 685389 |  |  |  | Back in service
73 | High rise | Not responding, INS mode on 34th floor w/ doors closed | 2014-01-17 | yes |  | 557574 |  |  |  | April 9th - Per Julietea, the parts arrived and Thyssen still working on it ***KH - March 4th - Spoke to Rick, this is a travelling cable issue. Cable has been ordered, waiting on delivery. Installation expected to take a few days as well. Reported to be functional at 0408hrs 14/4/24 -CF
62 | Mid rise | Near entrapment, shut down on 19 | 2014-04-24 | YES | [5 empty] | Started working sometime before 0407hrs 14-4-29. |  | April 28, 2014 at 1448
54 | LR | Thyssen left elevato on 15 with doors open and lights off | April 28 1615hrs | [6 empty] | Started working sometime before 0410hrs 14-4-30 |  | April 29, 2014 at 1409 hours
70 | High Rise | DRF on 42nd floor April 21st 1:45pm | 2014-04-21 | KH - Left voicemail for Kevin April 21st | [5 empty] | Functional as of 0330hrs 14/05/12 -CF
64 | Mid rise | Re-roping by Thyssen | Tuesday, May 6th 2014 | yes | [5 empty] | Functional as of 0330hrs 14/05/12 -CF | 2014-05-01
63 | Mid rise | Elevator out of service on 32nd floor, placed out for maintenance by Thyssen | Thursday, May 8th 2014 | Yes | [5 empty] | Functional as of 0330hrs 14/05/12 -CF
76 | Freight | Out of service on ground level | Friday, May 9th 2014 | [6 empty] | Functional as of 0330hrs 14/05/12 -CF
63 | MR | The elevator is out of service on the 33 floor with doors closed, the elevator was placed out of service by thyssen on (DIS) mode. | 5/26/2014 | Thyssen Aware | [7 empty] | Back in service on May 29, 2014
76 | Low Rise | Door Stuck | 2014-06-12 | Yes | [5 empty] | Reported to be functional at 0406hrs 14/6/13 -CF | will notify
61 | MR | The elevator is out of service on 19 floor with doors open and the lights off, the elevator was placed out of service due to no communication with (SOC) | 2014-06-21 |  | yes | Smartip#97411 |  |  |  | left voicemail **KH June 23rd - sent email to SmartIP** KH - June 24th - SmartIP to be on site today, Back in service
73 | HR | Stopped responding. Found on lobby w/ doors closed | 2014-06-24 | Yes |  | 750006 |  |  |  | Reported to be back in service June 24th 10am
69 | Mid Rise | Emergency call buttons are not working, no communication with SOC | 2014-06-27 |  |  | #97529 |  |  |  | NF - email sent to Smart Ip | Car # 69 went back in-service on June 30, 2014 at 0320 hrs
62 | MR | DRO on lobby | 01JUL14 | yes | [5 empty] | KH - Back in service per Matt from TKE July 2nd 7:45am
62 | MR | CSD mode on the 22nd floor | 2014-07-02 | YES | [5 empty] | Back in service
65 | MR | DRO mode, on lobby w/ doors open | 2014-07-07 | At 0422hrs July 7, 2014 |  | 766041 |  |  |  | Back in service
57 | LR | IND mode, doors closed, lights off on the 19th floor | 2014-07-26 | Yes | # 97969 | 779339 |  |  |  | back in service **KH - July 28th elevator not back in service, out due to communication. Smart IP emailed July 28th 7:45am**, back in service | SmartIp scheduled to be on site July 29th
54 | LR | DRF on lobby level | 2014-07-28 | Yes | [5 empty] | KH - Advised Rick from TKE July 28 7:45am, back in service
56 | LR | SFT mode on 2 w/ doors closed | 2014-08-03 | Yes, at 0522hrs 14/8/3 |  | 793691 |  |  |  | back in service as per TRR Duque at 1455
75 | Freight | Out of service | 2014-08-05 | Yes at 1751 |  | 795235 |  |  |  | back in service at 0928 8/6/2014
58 | LR | DRF mode on 8 w/ doors closed | 2014-08-03 | Yes, at 2125hrs 14/08/03, Arrived at 2303hrs |  | 793894 |  |  |  | Reparied at 2330hrs 14/08/03 -CF
65 | MR | Taken offline sometime during previous dayshift prior to 1500hrs due to "loose" cable noise. Thyssen was notified by TRR. | August 6, 2014 0700-1500hrs | Yes |  | Unknown |  |  |  | Back in service
82A | SOC Shuttle | Not responding to calls | August 6, 2014 1725hrs | Yes |  | Unknown |  |  |  | Repaired prior to 2130hrs 14-08-07
60 | Mid Rise | Went on SFT mode and got stuck on ground lobby with doors closed. | 24/08/2014 | Yes |  | 810547 |  |  |  | Back in service
74 | HR | INS Mode on 34th floor - taken out of service by Thyssen due to noise complaint | 2014-03-09 | Yes |  | 823704 |  |  |  | Back September 3 at 1440 hours
72 | HR | Showing Door Disconnect | 2014-09-12 | Yes |  | 833696 |  |  |  | Reported to be working 0458hrs 14-09-16
65 | MR | Taken out of service by SOC due to near entrapment | 2014-09-15 | YES | [5 empty] | Reported to be working 0458hrs 14-09-16
58 | LR |  | 2014-09-29 | Need To |  | 852712 |  |  |  | DRO on L w/ doors closed |  | September 30, 2014 at 0930
75 | Freight | Water leak | 2014-10-03 | Yes | [5 empty] | Back in service |  | October 3, 2014 at 1440
67 | HR | Screen shows IND but at actually stuck on lobby with doors closed at 0641 hours | 2014-10-04 | Yes-Dispatch |  | 858959 |  |  |  | Back In Service
75 | Freight | Contractor impacting doors from inside | 2014-10-04 | Yes - Dispatch | N/A | 859036 |  |  |  | Back In Service | Unknown | 10/04/2014 @ 1515 hours
82A | CF OPs | Elevator Modernization | 2014-09-01 | Locked out by TKE | [7 empty] | Back in service Oct 6th 1pm
64 | MR | Went on DRF mode and is stuck on 28 with doors closed at 2030 hours | 2014-10-03 | Yes- Dispatch |  | 858956 |  |  |  | Back In Service
77 | Parking | Out by security | 2014-10-06 | YES | [5 empty] | Back in service Oct 6th 11:25am
75 | Freight | Doors hit, stuck on P2 | 2014-10-09 | YES - Service desk as well as on site tech |  | 862858 |  |  |  | Back in service
81 | Shuttle | Stuck in between 45 and 46 | 2014-10-10 | Yes |  | 864404 |  |  |  | Technician could not fix it due to it be in overhang. Will be looked at by site techs on Tuesday |  | Back in service October 14th 9am
64 | MR | Stuck on lobby with doors open and lights on, light switch does not work. CSD mode. Signage has been placed | 2014-10-10 | YES - left message for Kevin from TKE Oct 14 re; doors not closing. Rick from TKE also advised. | [5 empty] | Back in service as per TRR Duque |  | 2014-10-14
57 | LR | Comunnication error with call button | 2014-10-25 | Smart IP contacted, message left |  | 99802 |  |  |  | KH - Email sent to Smart IP Oct 27th, awaiting ticket number KH - Oct 29 - per Smart IP, this is a bell isse, not communication. Advised Rick from TKE who will look at this today and advise back. *update - Oct 29 - issue is no alarm bell. TKE to repiar, elevator to stay o/s* Live status updated
67 | HR | Stuck on ground lobby with doors closed. Note: Computer monitor showing in-service. However, car not responding to lobby hall call button. | 2014-10-30 | Yes - Dispatch |  | 881231 |  |  |  | Back to normal at 0720 by Thyssen
68 | HR | Stuck on ground lobby with doors closed. Note: Computer monitor showing in-service. However, car not responding to lobby hall call button. | 2014-10-30 | Yes - Dispatch |  | 883064 |  |  |  | Back to normal at 0720 by Thyssen
73 | HR | Stuck on ground lobby with doors closed. Note: Computer monitor showing in-service. However, car not responding to lobby hall call button. |  | 2014-10-30 |  | 883065 |  |  |  | Back to normal at 0720 by Thyssen
73 | HR | No communication with SOC, emergency call button not working. | 2014-11-01 |  | Message Left |  |  |  |  | Back in service **KH - Smart IP was on site Nov 3 and communication was tested and ok
57 | LR | No alarm bell | 2014-10-25 | YES - KH advised Rick Oct 29th | [5 empty] | KH - Oct 29 - Initial report was no communication, Smart IP has determined this is a no alarm bell issue, TKE advised and will repiar. Elevator to stay o/s until this is fixed. |  | Alarm bell replaced and Back in service Nov 3rd 2:48pm
Up escalator |  | Knocking noise coming from escalators | 2014-11-03 | Yes, For business hours |  | 891660 |  |  |  | Back in service 9:22am Nov 4th
56 | Low Rise | Reports of elevator dropping several floors | 2014-11-05 | Yes |  | As Per Thyssen |  |  |  | Back in service
57 | Low Rise | Reports of elevator dropping several floors | 2014-11-05 | Yes |  | As per thyssen |  |  |  | Back in service
82A | C/C Ops | Malfunction | 06NOV14 | [6 empty] | Back in service
63 | Mid Rise | Out for maintenance by Thyssen | 2014-11-04 | Yes |  | As Per Thyssen |  |  |  | Reported to be working at 0455hrs 14-11-12 -CF |  | November 11 at 1423 hours
73 | HR | Complaint of car moving too fast when coming down to ground lobby from 33rd floor. | 2014-11-10 | Yes |  | 898275 |  |  |  | Reported to be working at 0455hrs 14-11-12 -CF
75 | Freight | Entrapment | 2014-11-12 | Yes |  | 898949 |  |  |  | Back in service
75 | Freight | Entrapment | November 12, 2014 | yes |  | 99387 | 12:26 | 12:39 | 15:07
75 | Freight | Elevator Hall Position Indicator, Lobby of Elevator #75 Freight | 2014-11-19 | Yes |  | 905486 |  |  |  | Back in service
62 | MR | DRO on lobby doors closed | 2014-11-25 |  |  | 911955 |  |  |  | Back in service Nov 25th 8:25am
53 | LR | Maintainance by Thyssen | 2014-11-04 | [6 empty] | Back in service (reported by TRR Duque) |  | November 26, 2014 at 1435 hours
73 | HR | Communication issues | 29NOV14 |  | 100466 |  |  |  |  | KH - email sent to Smart IP Dec 1- tech to be onsite Dec 1, back in service Dec 4
60 | MR | Comunications | 2014-12-06 |  | Yes V/M left at 0607 hours | No Communication #100584 |  |  |  | This elevator was found running at 0403hrs 14/12/09. The communication was tested and found to be working. -CF
61 |  | NF - stuck on the 30th floor DRF mode with the doors open | 10 Dec 2014 @ 10.57am | Yes - Service Desk & also voicemail for Thyssen tech |  | 934031 |  |  |  | Back in service
62 | MR | Stuck on ground. Doors closed | 17DEC14 | Yes |  | 939645 |  |  |  | Back in service

## TD West Tower (Tower #3) Histor
H | Group | Reason | Date out of Service | Thyssen Contacted | Smart IP | Ticket Number | Time Service Call to Thyssen was Placed (for After Hours & Critical Elevator Use Only) | Time Thyssen Arrived On Site (for After Hours & Critical Elevator Use Only) | Time Elevator was Placed Back in Service by Thyssen (for After Hours & Critical Elevator Use Only) | Status | Expected Return to Service | Actual Return to Service Date
92 | HR | DRF Mode | 2014-06-24 | Yes by ToAssist | [5 empty] | Reported to be working at 0447hrs 14/06/25 -CF
93 | High rise | DRF mode | 2013-11-29 | ToAssist Lucy spoke with Rick of Thyssen | [5 empty] | Returned to service
94 | HR | Ememrgency Communications failure | 2013-12-30 | [6 empty] | Communications were fine at 0506hrs 2014-01-02 -CF
92 | HR | On floor 21, display shows in-service, with doors half open. | 2014-01-07 | Yes |  | 542127 |  |  |  | Reported to be working at 0518hrs 2014-01-08 -CF
91 | HIR | "DRF" with doors closed on 29 | 2014-01-07 | Yes |  | 542127 |  |  |  | Reported to be working at 0518hrs 2014-01-08 -CF
93 | HR | "DSC" with doors open on 20 | 2014-01-07 | Yes |  | 542127 |  |  |  | Reported to be working at 0518hrs 2014-01-08 -CF
86 | High Rise | Wood paneling loose in the elevator leaving wires exposed | 2014-03-10 | [6 empty] | Back in service
91 | HR | Stuck between lobby and 2 w/ doors closed | 2014-04-17 | Immediate Service | 687736 |  |  |  |  | Repaired by Thyssen |  | April 16, 2014 at 0808
95 |  | SOC can not hear people on the elevator phone | 2014-04-27 | no, smart ip instead | Yes, they do not give reference #'s on weekends |  |  |  |  | Back in service |  | 2014-04-29
85 | High Rise | Placed on inspection by Thyssen due to tripping/slipping hazard. On CC w/ Lights Out | Thursday, May 8th 2014 | Yes | [5 empty] | Back in service May 9th 7:30am
88 | LR | on 7th floor doors open not responding | 2014-06-23 | yes |  | 748950 |  |  |  | Reported to be working at 0523hrs 14-06-24 -CF
83 | LR | Doors open on 7, not responding | 2014-06-21 | Yes |  | 748457 |  |  |  | Reported to be working at 0523hrs 14-06-24 -CF
92 | HR | DRF Mode | 2014-06-24 | Yes by ToAssist | [5 empty] | Reported to be working at 0447hrs 14/06/25 -CF
92 | HR | DRF on 24 | 25JUN14 | YES | [5 empty] | , Back in service
87 |  | DSC mode | 2014-07-08 | Yes |  | 767863 |  |  |  | Back in service at 1529 hours
86 | Low Rise | out of sevice at 1458 hours | 2014-07-11 | Yes By ToAssist | [5 empty] | Back in service
88 | LR | No communication when tested | 2014-09-08 |  | yes | #98189 |  |  |  | Back in servie Aug 12th - No communication issues found. **KH - Aug 11th 7:45am - email also sent to Smart IP.** Smart IP was left a message in there emergency mail box. They will call back and when they do Thyssen will be contacted.
85 | LR | DRF mode | 2014-08-12 |  | yes | 801367 |  |  |  | Back in Service by Matt from TKE Aug 13th 6:45am
85 | LR Freight | Metal grinding noise as doors open and close. It has been left offline on L w/ doors open and lights off | August 14, 2014 0059hrs | Yes |  | 802530 |  |  |  | Repaired overnight
85 |  | DSC mode | 2014-08-15 | yes |  | 803713 |  |  |  | back in service
86 | LR | Entrapment on 2nd floor | 25/08/14 | Yes |  | 811436 |  |  |  | Back in service
86 | LR | IND on 2 w/ doors closed due to entrapment | 2014-08-25 | [6 empty] | Reported to be working at 0515hrs 14/09/01 -CF
95 | Parking | No connection message appearing on screen. Out of service on P1 level | 2014-03-09 | Yes |  | 823706 |  |  |  | Back service Sept 3 8:10am
83 | LR | DRF mode on 6th floor with the doors closed | 2014-04-09 | YES | [5 empty] | KH Sept 4 - Matt from TKE working on this elevator today |  | Sept 04, 2014
85 |  | On CC doors closed. DRF mode. | 2014-09-11 | yes |  | 831670 |  |  |  | Back in service
91 | FR | DRF mode. On lobby | 2014-09-15 | Yes |  | 835253 |  |  |  | Repaired |  | 2014-09-15
85 | Freight | DRF at 1915 hours | 2014-09-17 | yes |  | 837373 |  |  |  | Back in service at 0042 hours 9/18/2014
91 | HR Freight | Out of Service - As per Thyssen tech Matt (Door operator needs to be replaced, waiting on parts) | 2014-09-25 | Yes - Matt @ 2.33pm
85 | LR Freight | Went on DSC mode and got stuck on 18th floor with doors open. | 2014-09-26 | Yes |  | 844442 | [5 empty] | 0712hrs 14-09-26 -CF
85 | Freight | DRF Mode (on ground, doors closed) | 2014-09-28 | Yes - Thyssen Dispatch - Immediate |  | 847106 |  |  |  | Back in service at 1030 hours |  | 2014-09-28
90 | HR | Doors constantly opening and closing IND mode on 18 | 2014-09-28 | Need to |  | 848229 |  |  |  | Back in service Sept 29th 8:30am
91 | HR | Malfunction | 2014-11-07 | Yes |  | 896650 |  | 1:50 | 23:21 | Back in service
86 | LR | Complaint of when doors close it stalls for several seconds before it opens again making a loud noise then closes | 2014-11-11 | Yes |  | 898276 |  |  |  | Reported to be working at 0455hrs 14-11-12 -CF
87 |  | Stuck on the 15th floor with doors open | 2014-11-17 | [6 empty] | KH - Nov 18 - advised Rick 7:45am. Back in service
89 | LR | DRF on Lobby w/ doors open | November 21, 2014 0757hrs | Yes - Service Desk |  | 907811 |  |  |  | Reported to be working at 0350hrs 14-12-04
90 | HR | D.S.C mode lobby level, door open. | 3rd Dec 2014 @ 2:53pm | Yes - Service Desk & Thyssen tech Matt |  | 927652 |  |  |  | Reported to be working at 0350hrs 14-12-04
91 | Highrise Freight | DRF mode on 32 with doors open. Was on service for contractors prior to going offline. No obvious signs of damage. |  | Yes, for immediate service |  | 932765 | 2015hrs | 2045hrs | 2105hrs | Working

## TD South Tower (Tower #4) Histo
Elevator | Group | Reason | Date out of Service | Thyssen Contacted | Smart IP | Ticket Number | Time Service Call to Thyssen was Placed (for After Hours & Critical Elevator Use Only) | Time Thyssen Arrived On Site (for After Hours & Critical Elevator Use Only) | Time Elevator was Placed Back in Service by Thyssen (for After Hours & Critical Elevator Use Only) | Status | Expected Return to Service | Actual Return to Service Date
115 |  | unresponsive via desk call button. The monitor indicating "RL". Doors closed on lobby. | 10/4/2014 at 0309 hours | Yes - Thyssen Dispatch |  | 858949 |  |  |  | Back in service
115 | HR | Stuck on lobby level; doors closed | 2013-11-27 | Yes - Barry - Nov 28th | [5 empty] | Found functional at 0524hrs 13-11-29. -CF
114 |  | Not stopping on requested floors | 2013-11-30 | [6 empty] | Back online December 2 0832hrs. -CF
115 |  | Not balancing itself on several floors | 2013-11-30 | [6 empty] | Back online December 2 0832hrs. -CF
121 | RYH | Internal Communication Error | 2013-12-17 |  | yes | 93374 |  |  |  | Phone tested after repair and elevator put back online at 1103hrs 13/12/19 -CF
121 | Royal York Parking | Near entrapment | 2014-01-05 | Yes |  | 538215 |  |  |  | Back in service
111 | HR | Dropped a few inches. Shut off on lobby level with lights out | 15 - Jan - 2014 | Yes - Rick @ 3.59 pm | [5 empty] | Back in service
115 | HR | The elevator is out of service on lobby with doors open and lights off, the elevator is out of service because it stopped on every floor and doors wouldn't open | 2013-12-22 | YES |  | 524969 |  |  |  | Found to be working at 0528hrs 14-01-20 -CF
106 | low rise | Door not closing on main lobby. Car on 6th floor w/ door open and lights off. | 2014-01-16 | Yes |  | M552 |  |  |  | Found to be working at 0528hrs 14-01-20 -CF
101 | low rise | loud noise | 2014-03-10 | yes |  | 622520 |  |  |  | Back in service
103 | low rise | stuck on 12th | 2014-03-10 | yes |  | 622520 |  |  |  | Back in service
114 | HR | On Lobby, doors closed, not responding | 2014-03-15 | Yes, for business hours |  | 628691 |  |  |  | Reported to be working at 0524hrs 14-03-21 -CF
107 | LR | Out of service due to tenant complaint of doors cycling | 27MAR14 | YES - KH - Spoke to Rick March 28th | [5 empty] | Reported to be working at 0424hrs 14-4-1 -CF
115 | high rise | , Doors open in main lobby (Doors are actually closed) | 2014-03-29 | yes |  | 666459 |  |  |  | Reported to be working at 0424hrs 14-4-1 -CF
114 | High Rise | Unresponsive to hall calls, placed out of service | 2014-04-11 | Yes | [5 empty] | Back in service by Rick from TKE April 14th 7:30am
115 | High Rise | Stuck on lobby level, non responsive | 2014-04-12 | Yes | [5 empty] | Back in service by Rick from TKE April 14th 7:30am
Small Escalator |  | The up small escalator is making squeaky noises, please notify Thyssen. - Alex Bo | April 14th | YES - Spoke to Rick April 14th 7:50am | [5 empty] | Escalator put back in service by Salim April 14th 7am
108 | Low Rise | Shut down by Thyssen due to bouncing | 2014-04-12 | Yes | [5 empty] | April 15th - back in service *** KH - Spoke to Rick April 14th 8am, he is currently working on this elevator
102 | LR | Entrapment | 1630hrs 14-4-15 | [6 empty] | Back in service
115 | HR | On lobby w/ doors closed. Not responding | 2014-04-23 | Yes |  | 691953 |  |  |  | Back in service
115 | High Rise | placed elevator #115 at tower 4 on service mode. There were multiple complaints of the doors not closing properly. The doors seemed to be holding open until the timer forced them closed. | 2014-04-25 | YES - KH spoke to Rick April 25th 7:25am | [5 empty] | Back in service |  | 2014-04-28
116 | Highrise | Taken offline on lobby due to complaints of vigorous shaking | 2014-04-26 | YES - KH spoke to Rick April 28th 7:40am | [5 empty] | back in service |  | 2014-04-28
104 | Low-Rise | unresponsive on lobby and could not get the car to move even with placed on independent service. The elevator car doors also 'clap' together when they close. | 27/05/14 | Thyssen Contacted | [5 empty] | Back in service
114 |  | Shutdown by Thyssen until June 02, 2014 @ 07:00 hours | 2014-05-30 | [6 empty] | KH - June 2nd - back in service per Rick from TKE 8:25AM | 2014-06-02
114 | HR | Per Thyssen until 0700 hrs | 02JUN14 | [6 empty] | Back in service
104 | LR | out of service on 20 | 03JUN14 | [6 empty] | Back in service per Matt from TKE June 4th 7:30am
108 | LR | Out of service on 20 | 03JUN14 | [6 empty] | KH - June 4th 7:30am Spoke to Matt from TKE, elevator left off for troubleshooting by Rick |  | Back in service as of June 6th
114 | HR | Per Thyssen | 13JUN14 | [6 empty] | Back in service June 16th 8:26am
109 | HR | Went out of service while car on independent service for GDI (Manuel). The door closed on its own in 35th floor and went up to 36th floor with doors closed | 2014-06-23 | yes |  | 748951 |  |  |  | Reported to be working at 0513hrs 14-06-24 -CF
114 | HR | Not responding, stuck on lobby | 2014-06-20 | Yes |  | 747550 |  |  |  | Reported to be working at 0513hrs 14-06-24 -CF
114 | HR | Out of service. The doors has difficulty closing, possibly due to wind pressure. Elevator #114 is grounded on the main lobby with doors open and lights off. | 30JUN14 | Yes | [5 empty] | NF - Thyssen tech Matt has been notified @9:09 am, Back in service
110 | HR | Doors cycling on lobby | 30Jun14 | YES | [5 empty] | KH - Back in service per Matt from TKE July 2nd 7:45am
118 | Parking | Not reposnding | 2014-07-02 | YES | [5 empty] | Reported to be working -CF
109 | LR | Greg Clark - hi thyssen has arrived at 79 wellington as of 0525 hours to look at elevator 109 that was taken out of service 2215 hours | 2014-07-03 | [6 empty] | Reported to be working -CF
Small Down Escalator | 64499608 | Not operational | [7 empty] | Reported to be working -CF
114 | HR | On lobby level w/ doors closed and not responding to calls | July 6, 2014 0530hrs | Yes |  | 765771 |  |  |  | Reported to be working July 7th 8:07am
114 |  | kept out of service from late afternoon Thursday July 10th to 0700 hours Friday July 11th, as per Thyssen instructions | 2014-07-10 | Yes | [5 empty] | Back in service July 11th 7am
104 | LR | Broken Tile, out of service on 20 | 25JUN14 | YES | [5 empty] | KH - Rick from TKE aware of this, elevator to be out for a couple of days CF - Reported to be working KH - July 11th - elevator still o/s per Julieta, Back in service
102 | HR | Out of service at 1758 | 2014-07-11 | yes |  | 771385 |  |  |  | CF - Reported to be working at 0511hrs 14/07/17
114 | HR | Card reader malfunction | 2014-07-15 | Yes |  | 773044 |  |  |  | CF - Reported to be working at 0511hrs 14/07/17
121 | royal york parking | elevator shaking | 2014-07-17 | Yes |  | 776113 |  |  |  | Back in service
114 | HR | Doors not opening on 20th floor lights off | 17JUL14 | [6 empty] | Back in service July 18th 7:30am
115 | HR | Doors recycling on 35th floor | 2014-07-15 | Yes |  | 773952 |  |  |  | back in service
114 | HR | Not opening on lobby, not leveling correctly | 2014-07-28 | YES | [5 empty] | back in service
115 | HR | Went out of service on lobby level w/ doors closed. Not responding to desk call button | 2014-08-02 |  |  | 794295 |  |  |  | back in service |  | 2014-08-05
117 | Freight | on lobby doors open. not responding | 2014-08-05 |  |  | 794295 |  |  |  | back in service |  | 2014-08-05
114 | HR | Doors closed on L and not responding to calls | 2014/08/08 2307hrs | Yes, at 2309hrs |  | 798242 |  |  |  | Back in Service |  | 0053hrs 2014/08/09
Large Down Escalator |  | Activation key switch at top end not working. Switch at bottom is working | 2014-08-14 | Yes |  | 803706 |  |  |  | Key switch repaired per Rick August 19th
115 | HR | On lobby with doors open | 2014-08-15 | yes |  | 804972 |  |  |  | Back in service August 19th 7am
118 | HR | Unknown Issue | 22/8/2014 | yes |  | 777487 |  |  |  | Back in service
110 | LR | moderation project | 22/08/14 | [6 empty] | Back in service
113 | HR | 20th doors open, not responding | Aug 29 Evening | Return to service Sept. 2nd |  | 821949 |  |  |  | Back in service Sept 2nd 7am
114 | HR | 20th doors open, not responding | Aug 29 Evening | Return to service Sept. 2nd |  | 821949 |  |  |  | Back in service Sept 2nd 7am
114 | HR | Out of service at 0248 unknown reason | 2014-09-03 | Yes |  | 823705 |  |  |  | Back in service Sept 4th 7:30am
115 | HR | On Lobby w/ doors closed, not responding | 2014-09-14 | 1847hrs 14-09-14 For service within 3 hours |  | 834161 |  |  |  | Reported to be working 0458hrs 14-09-16
110 |  | Making strange noises. out of service on lobby | 2014-09-14 | yes |  | 834201 |  |  |  | Reported to be working 0458hrs 14-09-16
115 | HR | On Lobby w/ doors closed, not responding | 9/16/2014 0525hrs | Yes |  | 835383 |  |  |  | Reported to be working at 0502hrs 14-09-17
115 | HR | not responding to hall call | 2014-09-19 | Yes |  | 839535 |  |  |  | Back in service Sept 22nd 7:23am
112 | HR | Doors won’t closed in main lobby | 2014-08-04 |  |  | 794295 |  |  |  | Back in service Sept 23rd 9:23am ****** Sept 21 - Rebuild initiated, expected back w/o 9/22 ---- Sept 10 - starter contact to be replaced. Part onsite but repairs focused on TW1 at the moment | Sept 23rd
121 | parking | Belt cable snapped and burned | 2014-09-18 | yes |  | 838438 |  |  |  | Sept 21- Belt has been ordered and expected back in service on Monday | Sept 22nd, 2014 | Back in service Sept 25th 10:07am
115 | HR | Door not closing | 2014-09-24 | Yes |  | 842372 | [5 empty] | Back in service on Sept 26, 2014
114 | HR | stuck on lobby w/ doors closed | 2014-09-26 | Yes, For buisness hours |  | 845198 |  |  |  | Back in service Sept 29th 8am
115 | HR | Stuck on L with doors closed | 2014-09-27 | Yes, For buisness hours |  | 847089 |  |  |  | Back in service Sept 29th 8am
115 | HR | Maintenance by Thyssen. | 2014-09-30 | [6 empty] | At 0455hrs 14-10-3 it was reported to be functional
Large Down Escalator |  | Escalator is functional. The key switch at the top the end is not working | 2014-09-25 | YES | [5 empty] | KH - Sept 29 Escalator is fully functional, there is another key switch that can be used. Rick from Thyssen aware of issue and will schedule work to have key switch looked at. This is a 2 person job and requires shutting the escalator down.
115 | HR | ON Lobby w/ doors closed and not responding to calls | October 3, 2014 0611hrs |  |  | 857900 |  |  |  | Back in service Oct. 3rd 7:56am
115 | HR | unresponsive via desk call button. The monitor indicating "RL". Doors closed on lobby. | 10/4/2014 at 0309 hours | Yes - Thyssen Dispatch |  | 858949 |  |  |  | Back in service
115 | HR | Doors cycling every 10 mnutes. Grounded on Lobby. | 10/05/1024 @ 1800 hours | Yes - Thyssen Dispatch |  | 859362 |  |  |  | Back in service |  | October 5, 2014 at 2010
115 | HR | Doors recycling on 33rd floor. Currently on 20th floor with doors open and lights turned off. | October 7, 2014 1836hrs |  |  | 860364 |  |  |  | Back in service |  | 2014-10-08
115 | HR | Unresponsive on lobby | 2014-10-10 | Yes |  | 863572 |  |  |  | Back in service 8:14am October 10th
112 | HR | Offline due to loose tiles in elevator, potential tripping hazard on 20 w/ doors open and lights off | 2014-10-12 | To Assist was advised | [5 empty] | KH - CLI to secure tiles eveing of October 14th, Back in service | October 15th | October 15th
110 | HR | Elevator not responding and not showing on display | -619144 | YES - KH spoke to Rick Nov 2nd 7:37am | [7 empty] | KH - Back in service Nov 3 8:55am
115 | HR | On Lobby doors closed, not responding | 2014-11-02 | YES - KH spoke to Rick Nov 2nd 7:37am | [7 empty] | KH - Back in service Nov 3 7:50am
117 | Freight | Stuck on lobby, doors closed at 03:11(HRS) | 2014-11-04 | Thyessen Contacted |  | 891719 | 3:15AM | 6:15AM | Approx. 6:18AM | TKE reported that they have resolved the issue and placed the elevator back in service |  | Nov 4th 6:18am
108 | LR | Reports of Elevator Jumping | 2014-11-05 16:45 | Yes | [5 empty] | Back in service Nov 6 8:46am
64499623 | Large Down Escalator | Taken offline due to grinding noise | 2014-11-05 | Yes |  | 894598 |  |  |  | Back in service Nov 6 8:43am
115 | HR | On Lobby w/ doors closed. Not responding to calls | 2014-11-08 | Yes, for regular daytime service |  | 896838 |  |  |  | At 1830hrs on Nov 9 the elevator spontaneously came back online without Thyssen being present. It will be left offline till it can be inspected. |  | Nov 10th 7:50am
114 | HR | Elevator unresponsive on Lobby with doors closed | 2014-11-09 |  |  | 896838 | [5 empty] | Nov 10th 7:50am
116 | HR | The elevator is out of service on 20 floor, the elevator was placed out of service by Thyssen due to the elevator jumping | 2014-11-13 | Yes |  | 902383 | November 15, 2014 at 0730 hrs | 1400 hrs |  | Tech could not fix it. Wiring problem. Back in Service | Monday, November 17, 2014 | Back in service Nov 17th
103 | LR | Issue with security system, to be returned to service in morning | 2014-11-18 | [6 empty] | Back in service
104 | LR | Issue with security system, to be returned to service in morning | 2014-11-18 | [6 empty] | Back in service
106 | LR | Issue with security system, to be returned to service in morning | 2014-11-18 | [6 empty] | Back in service
108 | LR | Issue with security system, to be returned to service in morning | 2014-11-18 | [6 empty] | Back in service
105 | LR | Issue with security system and button for the 11th floor is pushed in | 2014-11-18 | Yes |  | 904192 | 1:38 |  |  | KH Nov 18 - Rick from TKE to look into 11th floor button issue. Back in service
109 | HR | Not respnding on 28th floor doors closed | 2014-11-19 | Advised Rick via phone 11:55am as well |  | 905819 |  |  |  | Back in service
111 | HR | Wind pressure Elevator on lobby temporarily with doors open lights off | 2014-11-22 | No |  | N/A |  |  |  | Back in service per lobby desk Nov 24th 8:41am
108 | LR | Communication failure, taken out of service on the 2rd floor, doors closed. | 2014-11-22 | N/A | #100317 | Message Left *KH - Email sent to SmartIP Nov 24th 8:15am, awaiting ticket number and eta* |  |  |  | Back in service by TKE Nov 24th 9:35am, SmartIP will still check communication | SmartIP to be onsite Nov 24th | Nov 24th
110 | HR | Doors open and closing to various floors and buzzing ( OS, RS, BZ, EV ) | November 25, 2014 - 2.15pm | Yes - Service Desk |  | 912571 |  |  |  | Back in service Nov 25th 3:11pm
110 | HR | Went out of service on the 20th floor doors open | 2014-11-26 | yes |  | 913904 |  |  |  | Back in service
104 | LR | various floor buttons randomly lit up and became accessible when cleaners tried using elevator. | 2014-11-25 | yes |  | 913904 |  |  |  | Back in service
104 | LR | Buzzing sound, lights on and off | December 1, 2014 at 0600 | Yes |  | 923402 |  |  |  | Back in service Dec 1 8:13am per lobby desk
110 | HR | Elevator # 110 Inner Doors not closing stuck on the 33rd floor | November 27, 2014 at 1.23 pm | Yes - Service Desk |  | 918322 |  |  |  | Back in service reported by SG Malik |  | November 28, 2014 at 1530 hours
109 | HR | elevator # 109 reported by Torys descending from 33 floor the elevator skip 29 floor and doors open on 28 floor. | 2nd Dec 2014 @11.15 am | Yes - Service Desk & tech Rick |  | 926229 |  |  |  | Reported to be working at 0350hrs 14-12-04
108 | LR | Communications | 29NOV14 |  | 100466 |  |  |  |  | KH - email sent to Smart IP Dec 1 - tech to be onsite Dec 1, back in service Dec 4
104 | LR | All call buttons inside cab lit | 04DEC14 | [6 empty] | Back in service Dec 5 7:05am
104 | LR | NF - Elevator # 104 not responding on 18 floor doors open. | 5th Dec 2014 @8.35 am | Yes - Service desk |  | 930178 |  |  |  | At 0403hrs 14/12/09 this elevator was reported to be working
121 | Park | Offline on P5 w/ doors closed | December 6, 2014 0310hrs | Yes - For Immediate Service |  | 931413 | 0843hrs 14/12/07 | 1050hrs |  | At 1152hrs 14/12/07 Steve of Thyssen advised he could not repair the elevator and would have to speak to Rick about the repairs. |  | Dec 8th 11:30am
109 | HR | NF - Near Entrapment - Elevator taked out of servise by Thyssen as reported by SOC | 8th Dec 2014 | Yes - Service desk @ 2.07pm |  | 932306 | 2.07 pm |  |  | At 0403hrs 14/12/09 this elevator was reported to be working
117 | Freight | NF - not responding stuck on 2 floor . Doors closed | 9th Dec 2014 @ 1.29 pm | Yes - Service desk & tech Matt |  | 933357 |  |  |  | Reported to be working
Up Escalator | Lower Set | Status Indicator showing "Error" | 2014-12-12 | Yes - Service Desk |  | 935997 |  |  |  | Currently off - attempting to locate signs |  | Dec 12th 8:17am
UP (64499607) | Lower Set | Status indicator indicating "ER" | 12/15/2014 0400HRS | Yes - Service desk |  | N/A | 0435HRS |  |  | Called Thyssen, requested service, described specific escalator, Thyssen computer shows cancelled services for all 4 escalators |  | Dec 15th
109 | HR | Tenant rode elevator and it was shaking. | 2014-12-09 | Yes - Service desk |  | 931973 |  |  |  | At 0403hrs 14/12/09 this elevator was reported to be working KH - Dec 9th - per lobby desk, elevator is shut off per TKE. Back in service
UP (64499607) | Lower Set | Status indicator indicating "ER" | December 16, 2014 at 0530 hrs | Yes |  | 938643 | 0625 hrs |  |  | Back in service
117 | Freight | Currently stuck on the 2nd floor | 2014-12-17 | Yes - Service Desk |  | 940322 |  |  |  | Back in service Dec 17th
104 | LR | Keeps buzzing, all buttons are lit | 2014-12-21 | Yes |  | 944034 | 1:24 |  |  | Back in service
114 | HR | Stuck on lobby with the doors halfway open | 2014-12-31 | Yes |  | 983091 |  |  |  | Back in service
112 | HR | Doors won't close on lobby | 2014-12-31 | Yes, Business Hours |  | 990994 |  |  |  | Back in service
109 | HR | SOC - At 0946hrs 2 people became entrapped in elevator #109 between the 28th and 29th floors in tower 4. -Security and thyssen are making their way to the location | 2014-12-30 | Yes |  | 971788 |  |  |  | Back in service Jan 5th 2:15pm

## E&Y Tower (Tower #5) History
Elevator | Group | Reason | Date out of Service | Thyssen Contacted | Smart IP | Ticket Number | Time Service Call to Thyssen was Placed (for After Hours & Critical Elevator Use Only) | Time Thyssen Arrived On Site (for After Hours & Critical Elevator Use Only) | Time Elevator was Placed Back in Service by Thyssen (for After Hours & Critical Elevator Use Only) | Status | Expected Return to Service | Actual Return to Service Date
137 |  | Stuck on 18th Floor | 2013-12-31 | [6 empty] | Reported to be working at 0502hrs 2014-01-02 -CF
133 | MR | shut down on ground level (doors are closed) due to doors recycling and closing half way | 1/1/2014 -CF | Yes |  | 530083 |  |  |  | Back in service
145 | DX | Stuck on 1st floor | 2014-01-05 | Yes |  | 538221 |  |  |  | 6/1/2014 Back in Service
133 | MR | Not responding, on ground with doors open | 2014-01-08 | Yes |  | 543221 |  |  |  | Back in service
Freight |  | Stuck on P1 with the doors open, placed off service by S/G Matovu | 2014-01-10 | Yes | [5 empty] | Back in Service
142 | HR | Maintenance | 14JAN13 | [6 empty] | back in service
141 | HR | shut down at 1500 hours, due to mis leveling. Car is on the ground level, doors closed. | 16 - Jan 2014 | Yes - Rick @ 3.09pm | [5 empty] | Found to be working at 0523hrs 14-01-20 -CF
145 | DX | Not responding, unknown floor | 2014-01-18 | Called Thyssen morning of 14-01-20, they advised call has already been placed | [5 empty] | back in service
130 | low rise | stuck on the 7th floor with doors not closing | 2014-01-20 | yes |  | 558636 |  |  |  | back in service
143 | Freight | Functions only in service, not free-run | March 08, 2014 at 0750 | yes |  | 621032 |  |  |  | back in service March 9, 2014 at 1230
137 | MR | Entrapment | 1337hrs 2014-03-26 | YES | [5 empty] | Reported to be working at 0454hrs 14-4-2 -CF
139 | HR | Sudden drops | 2014-04-18 | yes |  | 687967 |  |  |  | Back in service
144 |  | Not responding | 2014-04-21 | Yes |  | 688503 |  |  |  | Thyssen put parking elevator #144 back in service at 0750 hours.
141 | high-rise | Found on 23rd floor with doos opening & closing. Placed on IND with lights out on 23rd floor | 2014-06-02 | Thyssen Contacted |  | 730898 |  |  |  | KH - June 2nd - back in service per Rick from TKE 8:25AM
133 | MR | Stuck on Con | 02JUN14 | [6 empty] | Back in service
136 | MR | Stuck on 10 | 02JUN14 | [6 empty] | Back in service
137 | mid-rise | On lobby with doors closed | 2014-05-30 | Thyssen Contacted |  | 730899 |  |  |  | KH - June 2nd - out for maintenance by Rick from TKE, Back in service
130 | LR | on 7 w/ doors closed | 2014-06-12 | Yes |  | 741550 |  |  |  | Back in service
141 | HR | 1/2 foot above lobby level w/ doors open | 2014-07-07 | At 0354hrs July 7, 2014 |  | 766039 |  |  |  | back in service
133 | Mid rise | out of service | August 4th, 2014 |  |  | 794296 |  |  |  | Back in service | 2014-08-05
131 | LR | NF - 2:59pm. (Low-rise) was reported mislevelling with doors opening on the 5th floor, To-assist was advised. Thyssen has been on site and has left the car O/S for the night | 2014-08-20 | Yes | [5 empty] | Back in service
143 | FR | flooded pit | 2014-09-15 | yes | [5 empty] | Back in service Sept 16th 8:24am
134 | MR | the door operator linkage broke and doors were closing half-way. | 2014-09-24 | Yes- Thyssen took off servie | [7 empty] | Back in service on Sept 26, 2014
130 | LR | Stuck on 8 w/ doors closed | 9/29/2014 0835hrs | YES | [5 empty] | back in service | 2014-09-30
143 | Freight | Stuck on the 30th with doors open | 2014-10-09 | Yes |  | 863543 |  |  |  | Back in service
136 | MR | Entrapment | 2014-10-02 | Yes - Thyssen Dispatch |  | 857423 |  |  |  | back in service
131 | LR | Doors Cycling on 9th floor | 2014-10-09 | [6 empty] | Back in service
142 | HR | Not Responding to calls. | 10/14/2014 2246hrs | Yes - Thyssen Dispatch |  | 866209 |  |  |  | On L w/ doors closed, Back in service
143 | FR | flooded pit | 2014-09-15 | yes | [5 empty] | Back in service Sept 16th 8:24am
134 | MR | the door operator linkage broke and doors were closing half-way. | 2014-09-24 | Yes- Thyssen took off servie | [7 empty] | Back in service on Sept 26, 2014
130 | LR | Stuck on 8 w/ doors closed | 9/29/2014 0835hrs | YES | [5 empty] | back in service | 2014-09-30
143 | Freight | Stuck on the 30th with doors open | 2014-10-09 | Yes |  | 863543 |  |  |  | Back in service
136 | MR | Entrapment | 2014-10-02 | Yes - Thyssen Dispatch |  | 857423 |  |  |  | back in service |  | 2014-12-15
131 | LR | Doors Cycling on 9th floor | 2014-10-09 | [6 empty] | Back in service
142 | HR | Not Responding to calls. | 10/14/2014 2246hrs | Yes - Thyssen Dispatch |  | 866209 |  |  |  | On L w/ doors closed, Back in service
141 | HR | on lobby with doors open | 2014-09-20 | Yes - Thyssen Dispatch |  | 870679 |  |  |  | Back in service
130 | LR | Communication error with call button | 2014-10-25 | Smart IP contacted, message left |  | 99802 |  |  |  | KH - Oct 27th - back in service 7:47am by Angel and TKE (communication was tested and was ok) Smart IP still requested to come in. Email sent to Smart IP, awaiting ticket number. Oct 27th - Smart IP came and tested, communication was working, there is just a delay
135 | MR | Communication error with call button | 2014-10-25 | Smart IP contacted, message left |  | 99082 |  |  |  | KH - Oct 27th - back in service 7:37am by Angel and TKE (communication was tested and was ok) Smart IP still requested to come in. Email sent to Smart IP, awaiting ticket number. Oct 27th - Smart IP came and tested, communication was working, there is just a delay
139 | HR | Wire thru Motor - prioritize after 33/34 | 2014-06-18 | Yes - Thyssen Dispatch |  | 839578 |  |  |  | Back in service Nov 4th 2:12pm
Up Escalator |  | Banging Noise from escalator. | 2014-11-03 | Yes, For business hours |  | 891662 |  |  |  | Back in service Nov 4th 8:20am
143 | Freight | Doors opening and closing repeatedly on all floors. Otherwise functional | 11/6/2014 0045hrs | Yes, for immediate service -CF |  | 894590 | 0050hrs |  | 7:20 | Back in service Nov 6th 7:20am
135 | MR | Taken offline due to missleveling. On Lobby w/ doors closed | 11/5/2014 1205hrs | YES | [5 empty] | Back in service Nov 6th 8:23am
139 |  | Not moving, doors open, on lobby | 2014-11-06 | Yes - Thyssen Technicians | [5 empty] | Back in service Nov 10th 1:56pm
140 | HR | Stuck on 25 w/ doors closed | 2014-11-11 | Yes |  | 898277 |  |  |  | Reported to be working at 0455hrs 14-11-12 -CF
139 | HR | Out of service due to entrapment | November 13th 2014, 06:11 | Yes | N/A | N/A | 6:11 | 7:05 | N/A | Back in service Nov 24th 9:30am | N/A
130 | LR | Entrapment | 2014-11-19 | Yes |  | 906458 | 2230 | 2250 | N/A | Back in Service 1:30pm Nov 25th
140 | HR | Out by Thyssen due to entrapment | 2014-11-22 | Yes - Out By Thyssen |  | 908773 | 11:32 | 11:50 | N/A | Back in service | N/A | November 26, 2014 at 1426 hours
141 | HR | Not responding on G with doors closed | 2014-11-26 | Yes |  | 914900 | 18:36 |  |  | Back in service | N/A
144 | Parking | Lighting not operational | 2014-11-28 | Yes |  | 918830 | 5:48 |  |  | Back in service Nov 28th 8:07am
Escalator | Down | Slip & Fall - Canoe Employee | 12/02/2014 @ 1913 hours | Yes - Dispatch |  | 924905 | 1915 hours |  |  | Reported to be working at 0350hrs 14-12-04
134 | MR | Entrapment | 10:59 | Yes |  | 933275 | 1222 |  |  | Back in service Dec 9th 3:15pm
134 | MR | SOC Liliyan -Enable safety for Modern Niagara contractors who are installing a new AC unit in the machine room. Service will return early morning. | 2014-12-10 | N/A | N/A | N/A |  |  |  | Back in srvice morning of Dec 11
139 | HR | Stuck on 29 with doors open | 12/12/2014 at 2120HRS | Yes |  | 937450 | 0435HRS |  |  | Back in service
136 | MR | Entrapment | 2014-10-02 | Yes - Thyssen Dispatch |  | 857423 |  |  |  | back in service |  | 2014-12-16
136 | MR | Entrapment | 12/1/2014 1930hrs | Yes |  | 924524 | 1934hrs | 1957hrs |  | Back in service as per Thysen at 0915 hours |  | 2014-12-16
130 | LR | elevator # 130 it is not responding from floor 4. | 16th Dec 2014 @ 10.49am | NF - Thyssen Service desk Ref # 938986 |  | 938986 |  |  |  | Back in service. |  | 2014-12-16 14:20
136 | MR | Maintenance by Thyssen | 16DEC14 | [6 empty] | Back in service Dec 17 7:30am
145 | DX | On idependant for unknown reason | Unknown | [6 empty] | Back in service January 2nd
143 | Freight | On 30, doors open. | 2015-01-02 | Yes |  | 994181 |  |  |  | Back in service January 2nd
143 | Freight | Stuck on 16th floor dooors open (and will not close) | 2015-01-02 | Yes |  | 994772 |  |  |  | In service

## 95 Wellington (Tower #6) Histor
Elevator | Group | Reason | Date out of Service | Thyssen Contacted | Smart IP | Ticket Number | Time Service Call to Thyssen was Placed (for After Hours & Critical Elevator Use Only) | Time Thyssen Arrived On Site (for After Hours & Critical Elevator Use Only) | Time Elevator was Placed Back in Service by Thyssen (for After Hours & Critical Elevator Use Only) | Status | Expected Return to Service | Actual Return to Service Date
203 | HR | Stuck on L with doors closed | November 17th, 2013 | LM- Spoke to Barry | [5 empty] | KH -Back in service January 10th at 10am per Claudia at lobby desk |  | Janaury 10th, 2014
209 |  | Pits filled with water. Plan Group and ACML currently working on issue from earlier in the day | 2014-03-20 | Yes | [5 empty] | In service
Escalator: 111 | Up | Out of service by Thyssen for maintenance | Thursday, May 8th 2014 | [6 empty] | Reported to be working at 0451hrs 14-05-12 -CF
203 | HR | Not responding, unknown floor | 2014-06-03 | YES |  | 732616 |  |  |  | Back in service June 4th |  | 2014-06-04
203 |  | elevator stops responding, located on the 16th floor | 2014-06-27 |  |  | 755396 |  |  |  | Back in service
210 |  | Out of service | 27JUN14 |  |  | 756659 |  |  |  | Back in service
207 | LR | The service key switch is non-functional. Whether turned to service or free run the elevator remains on free run. | 2014-07-15 | Yes |  | 773944 |  |  |  | back in service
206 | LR | Out of service | 2014-07-21 | yes |  | 778386 |  |  |  | CF - Reported to be running at 0428hrs 14-07-23
202 | HR | Out of service on the 21st floor with doors closed. | 2014-08-01 | Yes |  | 790957 |  |  |  | back in service |  | 0801 2014-08-01
203 | HR | Out of service on the 20th floor with doors open and 3 feet above ground level. Thyssen advised they have fixed the elevator and are awaiting a technican in the morning at 8 am in order to confirm it is working. | 2014-08-06 | Yes |  | 796353 |  |  |  | Thyssen came in and the tech believes the elevator is repaired but didn't want to put it online till the day crew confirms it is working. The doors have been closed. Back in service |  | Reported to be working at 0425hrs 14-08-08
203 | HR | Stuck on L w/ doors closed. Not responding to calls | 2014/08/08 2025hrs | Yes at 2026hrs |  | 798224 |  |  |  | reported to be working at 2109hrs 14-08-08 |  | reported to be working at 2109hrs 14-08-08
203 | HR |  | Does not respond | 26AUG14 | Yes |  |  |  |  | 814457 | Back in service
203 | HR | Stuck metre of ground, doors closed | 2014-09-23 | Yes |  | 842371 |  |  |  | back in service |  | 2014-09-24
206 | LR | Maintenance by thyssen | 2014-09-23 | [8 empty] | Reported to be working at 0455hrs 14-09-28 -CF
208 | LR | Near Entrapment - Secured on lobby | 2014-10-02 | Yes - Thyssen Dispatch & Matt |  | 857687 |  |  |  | On Lobby w/ doors closed | Back in service Oct 7 7:24am
203 | HR | Unresponsive | 2014-09-27 | Yes - Thyssen Dispatch - Business |  | 846792 |  |  |  | Reported to be working at 0455hrs 14-10-15 -CF
209 | Parking | Unresponsive | 2014-10-14 | Yes |  | 866051 |  |  |  | On P1 with doors open | Back in service 8:25am October 15th | Wednesday, October 15, 2014
201 | HR |  | Stuck on 19, doors closed | 15OCT14 | [6 empty] | Back in service
207 | LR | Stuck on 7th floor, doors closed unknown reason | 2014-10-27 | Yes |  | 876653 |  |  |  | Back in service |  | 10/28/2014 0901 hours
208 | LR | Entrapment | 2014-11-25 | Yes - Dispatch & On Sites |  | 912712 |  |  |  | Back in service as per E. Turner's e-mail |  | November 26, 2014 at 1100 hours
206 | LR | Not moving, stuck on ground with doors open | 2014-11-27 | Yes |  | 918792 | 22:07 | 23:15 | 23:30 | Functioning
201 | HR | THis elevator is offline on an unknown floor. When it went offline the hall call button on the lobby level stopped functioning | December 4, 2014 0600hrs |  |  | 928082 |  |  |  | At 0701hrs Thyssen took control of 201 at which point the hall call buttons started working. 201 is currently offline, back in service
210 | Freight | Not responding, 1" below the ground floor w/ doors open | DEcember 6, 2014 1542hrs | Yes, for immediate service |  | 931252 | 1545hrs | 1800hrs | 1810hrs | back in service
207 | LR | near entrapment | 2014-11-21 | yes |  | 908678 |  |  |  | Back in service Dec 11th